Project Name:	London Creek 230 kV Lines

Project Description

Increase capacity of line to alleviate congestion.

| Projected In-Service Date for Base Reliability Plan | 2016 |
| --- | --- |
| Earliest Projected In-Service Date For Resource Supply Option | 2015 600 MW Import to CPLE from Duke |
| Project Lead Time | 3 years |
| Estimated Cost | $20 – 25 M |

Narrative Description of the Need for this Project

The London Creek Lines will achieve 100% of their conductor rating in the 2015-2016 timeframe. The lines are most heavily loaded when there is an Oconee unit outage for the loss of the parallel line. The line is sensitive to south to north transfers. Increased import from SOCO lowers loading on the London Creek lines and can delay the need for upgrade.

Transmission Solutions Considered

Bundle the line Reactors

Why this Project was Selected as the Preferred Solution

Duke does not routinely use reactors to redistribute flows on the system. Reactors would increase losses and cause increased flow on the underlying 100 kV system. Bundling of the line will alleviate the loading concern and reduce system losses.