## Branch Violations
| 2011 Summer Branches with MVA flow > 90.0 % of nominal rating | Base TRM (3600MW) Import |  |  |  |  | Base TRM + 600MW/1200MW Import | [5 empty] | DK 600MW + TRM Import |  |  |  | SCEG 600MW + TRM Import |  |  |  | SCPSA 600MW + TRM Import |  |  |  | VAP 600MW + TRM Import |  |  |  | SOCO 600MW + TRM Import |  |  |  | TVA 600MW + TRM Import |  |  |  | AEP 600MW + TRM Import |  |  |  | AEP/AEP 1200 MW + TRM Import |  |  | AEP/VAP 1200 MW + TRM Import
Line | From bus / To bus / CKT | Base HR DN | Base BR1 DN | Max | Base Solution Yr | Base Solution | Max % | % Impact | Source(s) | Max Acc Yrs | Earliest Need | Rating (MVA) | HR DN | BR1 DN | MaxDu | Acc Yrs | HR DN | BR1 DN | Max SCG | Acc Yrs | HR DN | BR1 DN | Max | Acc Yrs | HR DN | BR1 DN | max | Acc Yrs | HR DN | BR1 DN | Max | Acc Yrs | HR DN | BR1 DN | Max | Acc Yrs | HR DN | BR1 DN | Max | Acc Yrs | HR DN | BR1 DN | Max | HR DN | BR1 DN | Max | Contingency | Import Comment
Richmond-Newport 500 kV | 20377 RICHMOND 500 337 8NEWPORT 500 1 | 108.1 | 109.6 | 109.6 | 2007.16 | * | 118.5 | 8.9 | Duke/SOCO | 3.56 | 2003.6 | 1350 | 117.1 | 118.5 | 118.5 | 3.56 | 114.3 | 115.8 | 115.8 | 2.48 | 112.3 | 113.73 | 113.73 | 1.652 | 112.4 | 113.8 | 113.8 | 1.68 | 117 | 118.5 | 118.5 | 3.56 | 116.7 | 118.2 | 118.2 | 3.44 | 115.2 | 116.7 | 116.7 | 2.84 | [6 empty] | PHSH1-ANSON230_&_PHSH2-ANSON230 | Phase angle DeltaP
Marion - Weatherspoon 115kV | 20654 DILLON T 115 20632 MARION 115 1 | 84.5 | 94.9 | 94.9 |  | OpProc6 | 117.4 | 22.5 | SC |  | 2004.04 | 97 | 91.4 | 100.6 | 100.6 |  | 103.5 | 112.7 | 112.7 |  | 108.3 | 117.4 | 117.4 |  |  | 99.1 | 99.1 |  | 96.5 | 105.7 | 105.7 |  | 94.7 | 103.9 | 103.9 |  | 92.1 | 101.3 | 101.3 |  | 91.8 | 101 | 101 | <90 | 98.8 | 98.8 | 20663 LATTA 230 20682 DILLMP T 230 1 | Operating Procedure
Wake 500/230 kV Bank 1 / 2 | B$0024 1.00 20183 WAKE 500 1 / 2 | 97.6 | 93.4 | 97.6 | 2015.56 | Beyond /Follow | 110 | 12.4 | AEP/VAP | 4.96 | 2010.6 | 1000 | 106.7 | 102.4 | 106.7 | 3.64 | 106.9 | 102.7 | 106.9 | 3.72 | 106.8 | 102.5 | 106.8 | 3.68 | 108.8 | 104.6 | 108.8 | 4.48 | 107.4 | 103.2 | 107.4 |  | 107.6 | 103.5 | 107.6 | 4 | 108.1 | 104 | 108.1 | 4.2 | 109.3 | 105.2 | 109.3 | 110 | 105.8 | 110 | 3Wnd: OPEN B$0045 2 / 1 | New project (upgrade/ add bank)
Sutton-Castle Hayne 230kV | 20039 SUT 3 F 230 20554 9THORG T 230 1 | 106.1 | 101.7 | 106.1 |  | OpProc2 | 107.3 | 1.2 | SCEG/SC |  | 2008.08 | 590 | 106.6 | 102.3 | 106.6 |  | 107.3 | 102.8 | 107.3 |  | 107.3 | 103 | 107.3 |  | 105.8 | 101.7 | 105.8 |  | 106.9 | 102.5 | 106.9 |  | 106.7 | 102.4 | 106.7 |  | 106.4 | 102.2 | 106.4 |  | 106.1 | 101.9 | 106.1 | 105.6 | 101.5 | 105.6 | BR1-BARCK230_&_BR2-BARCRK230 | Local /Follow
Biscoe-Asheboro East 115 kV | 20303 SEAGROVE 115 20304 E14-ULAH 115 1 | 100.3 | 84.9 | 100.3 |  | OpProc1 | 107.1 | 6.8 | SCEG |  | 2008.16 | 148 | 106.4 | 90.6 | 106.4 |  | 107.1 | 91.2 | 107.1 |  | 106.9 | 91.1 | 106.9 |  | 103.2 |  | 103.2 |  | 106.4 | 90.6 | 106.4 |  | 105.9 | 90.1 | 105.9 |  | 104.8 |  | 104.8 |  | 103 | <90 | 103 | 101.4 | <90 | 101.4 | 20309 BISCOE W 230 20332 ASHEB 230 1 | New project (uprate)
Falls 230/115 | 20185 FALLS 115 20182 FALLS 230 1 | 104.7 | 104.1 | 104.7 | 2012.72 | Add Bank | 106.7 | 2 | Duke | 0.8 | 2011.92 | 300 | 106.7 | 106.2 | 106.7 | 0.8 | 106.1 | 105.5 | 106.1 | 0.56 | 106 | 105.4 | 106 | 0.52 | 105.6 | 105.1 | 105.6 | 0.36 | 106.2 | 105.6 | 106.2 | 0.6 | 106.3 | 105.7 | 106.3 | 0.64 | 106.3 | 105.7 | 106.3 | 0.64 | 106.1 | 105.5 | 106.1 | 105.4 | 104.9 | 105.4 | HNDRSN-FRNKLNTN115_&_HNDRSN-E18_KITT115 | Project good for horizon
Fay-Fay Ft. Bragg Woodruff230 kV | 20388 P3-FAYRR 230 20387 P1-FAY 0 230 1 | 97.4 | 73.9 | 97.4 | 2012.04 | Replace Equip | 105.9 | 8.5 | SC | 3.4 | 2008.64 | 637 | 101.7 |  | 101.7 | 1.72 | 105.1 |  | 105.1 | 3.08 | 105.9 |  | 105.9 | 3.4 | 100.5 |  | 100.5 | 1.24 | 103.6 |  | 103.6 | 2.48 | 102.9 |  | 102.9 | 2.2 | 101.8 |  | 101.8 | 1.76 | 100.9 | <90 | 100.9 | 99.7 | <90 | 99.7 | 20387 P1-FAY 0 230 20389 P2-FAY E 230 1 | Project good for horizon
Rockingham-West End 230 kV Line | 20638 WDSB T 230 20348 RKH 230 1 | 100 | 87.2 | 100 |  | OpProc5 | 105.8 | 5.8 | SCEG/SC |  | 2008.68 | 539 | 103.6 | 90.5 | 103.6 |  | 105.7 | 92.6 | 105.7 |  | 105.8 | 92.7 | 105.8 |  | 102.1 |  | 102.1 |  | 104.8 | 91.7 | 104.8 |  | 104.3 | 91.2 | 104.3 |  | 103.3 | 90.2 | 103.3 |  | 102.2 | <90 | 102.2 | 101 | <90 | 101 | 20348 RKH 230 20361 WEST END 230 1 | New project (rebuild/ recond)
Tilley-Biscoe 115 kV | 20004 TIL 1-4H 115 20302 E14-TROY 115 1 | 96.5 | 83.1 | 96.5 |  | OpProc1 | 105.6 | 9.1 | Duke |  | 2008.76 | 269 | 105.6 | 91.6 | 105.6 |  | 104.4 | 90.1 | 104.4 |  | 103.7 |  | 103.7 |  | 100.4 |  | 100.4 |  | 104.3 |  | 104.3 |  | 103.9 |  | 103.9 |  | 102.6 |  | 102.6 |  | 100.1 | <90 | 100.1 | 97.9 | <90 | 97.9 | 20347 ABRDN RD 230 20348 RKH 230 1 | Operating Procedure
Laurinburb 230/115 Bank 1 / 2 | 20421 LAURINBG 115 20424 LAURINBG 230 1 / 2 | 98.6 | 96.8 | 98.6 | 2011.56 | Replace | 103.8 | 5.2 | SC | 2.08 | 2009.48 | 200 | 100.3 | 98.5 | 100.3 | 0.68 | 102.8 | 101 | 102.8 | 1.68 | 103.8 | 102 | 103.8 | 2.08 | 99.7 | 97.9 | 99.7 | 0.44 | 101.3 | 99.6 | 101.3 | 1.08 | 100.9 | 99.2 | 100.9 | 0.92 | 100.3 | 98.5 | 100.3 | 0.68 | 100 | 98.2 | 100 | 99.4 | 97.6 | 99.4 | 20421 LAURINBG 115 20424 LAURINBG 230 2 / 1 | Project good for horizon
Fay-Fay East 230 kV | 20387 P1-FAY 0 230 20389 P2-FAY E 230 1 | 93.4 | 69.1 | 93.4 | 2013.64 | Replace Equip | 103.6 | 10.2 | SC | 4.08 | 2009.56 | 637 | 99 |  | 99 | 2.24 | 102.7 |  | 102.7 | 3.72 | 103.6 |  | 103.6 | 4.08 | 97.6 |  | 97.6 | 1.68 | 101.1 |  | 101.1 | 3.08 | 100.4 | 103.4 | 103.4 | 4 | 99 |  | 99 | 2.24 | 98 | <90 | 98 | 96.6 | <90 | 96.6 | 20387 P1-FAY 0 230 20388 P3-FAYRR 230 1 | Project good for horizon
Fay 230/115 kV Bank 1/2 | 20387 P1-FAY 0 230 20392 FAY 115 1 / 2 | 91.4 | 95.4 | 95.4 | 2012 | Replace Banks | 103.6 | 8.2 | SCEG | 2.44 | 2009.56 | 200 | 99.4 | 103.4 | 103.4 | 3.2 | 99.5 | 103.6 | 103.6 | 3.28 | 99.4 | 103.5 | 103.5 | 3.24 | 98.3 | 102.3 | 102.3 | 2.76 | 99.4 | 103.4 | 103.4 | 3.2 | 99.3 |  | 99.3 | 1.56 | 99 | 103 | 103 | 3.04 | 98.3 | 102.3 | 102.3 | 97.6 | 101.6 | 101.6 | 20387 P1-FAY 0 230 20392 FAY 115 2 / 1 | Project good for horizon
Rockingham - Anson 230 kV Blk | 20350 PH SH 1B 230 20985 ANSON 230 1 | 92.4 | 93.4 | 93.4 |  | OpProc5 | 103.4 | 10 | Duke |  | 2009.64 | 398 | 102.8 | 103.4 | 103.4 |  | 98.3 | 98.8 | 98.8 |  | 95.9 | 96.6 | 96.6 |  | 96.7 | 97.6 | 97.6 |  | 101 | 101.1 | 101.1 |  | 100.9 | 101.5 | 101.5 |  | 99.7 | 100.3 | 100.3 |  | 95.5 | 96.3 | 96.3 | 92.7 | 93.6 | 93.6 | 337 8NEWPORT 500 20377 RICHMOND 500 1 | New project
Rockingham - Anson 230 kV Wht | 20349 PH SH 2W 230 20985 ANSON 230 1 | 92.2 | 93.2 | 93.2 |  | OpProc5 | 103.2 | 10 | Duke |  | 2009.72 | 398 | 102.6 | 103.2 | 103.2 |  | 98.1 | 98.7 | 98.7 |  | 95.7 | 96.4 | 96.4 |  | 96.6 | 97.4 | 97.4 |  | 100.8 | 101.3 | 101.3 |  | 100.7 | 101.3 | 101.3 |  | 99.5 | 100.1 | 100.1 |  | 95.3 | 96.1 | 96.1 | 92.5 | 93.5 | 93.5 | 337 8NEWPORT 500 20377 RICHMOND 500 1 | New Project
Durham-Cary Reg Pk 230 | 20091 BRIERCK 230 10117 DURHAM 230 1 | 93.2 | 74.9 | 93.2 |  | OpProc3 | 102.8 | 9.6 | Duke |  | 2009.88 | 539 | 102.8 |  | 102.8 |  | 99.3 |  | 99.3 |  | 99.3 |  | 99.3 |  | 100.2 |  | 100.2 |  | 100.3 |  | 100.3 |  | 100.6 |  | 100.6 |  | 101 |  | 101 |  | 100.1 | <90 | 100.1 | 99.3 | <90 | 99.3 | METHOD-PRISONF230_&_METHOD-BLUERDG230 | New project
Tilley-Biscoe 115 kV | 20683 BURNETTE 115 20302 E14-TROY 115 1 | 93.5 | 80.2 | 93.5 |  | OpProc1 | 102.6 | 9.1 | Duke |  | 2009.96 | 269 | 102.6 |  | 102.6 |  | 101.4 |  | 101.4 |  | 100.7 |  | 100.7 |  | 97.4 |  | 97.4 |  | 101.3 |  | 101.3 |  | 100.9 |  | 100.9 |  | 99.6 |  | 99.6 |  | 97.1 | <90 | 97.1 | 95 | <90 | 95 | 20347 ABRDN RD 230 20348 RKH 230 1 | Operating Procedure
Sutton-Delco 230 kV | 20039 SUT 3 F 230 20582 DELCO 230 1 | 88.5 | 68.1 | 88.5 |  | OpProc2 | 102 | 13.5 | SCEG/SC |  | 2010.2 | 478 | 98.9 |  | 98.9 |  | 102 |  | 102 |  | 102 | 90.3 | 102 |  | 96.7 |  | 96.7 |  | 100.6 |  | 100.6 |  | 99.9 |  | 99.9 |  | 98.6 |  | 98.6 |  | 97.7 | <90 | 97.7 | 95.8 | <90 | 95.8 | BR1-BARCK230_&_BR2-BARCRK230 | Operating Procedure
Camden-Camden Junction 115 kV | 20725 CAMDEN 115 20716 CAMCTY02 115 1 | 85.3 | 82.9 | 85.3 | 2016.88 | Beyond /Follow | 98.6 | 13.3 | SCEG | 5.32 | 2011.56 | 108 |  |  |  |  | 98.6 | 96.1 | 98.6 | 5.32 | 98.6 | 96.2 | 98.6 | 5.32 | [22 empty] | 20725 CAMDEN 115 20731 I-DUP CA 115 1 | New project (uprate)
Biscoe-Asheboro East 115 kV | 20290 I-OLVRRB 115 20304 E14-ULAH 115 1 | 91.8 | 76 | 91.8 |  | OpProc1 | 98.6 | 6.8 | SCEG |  | 2011.56 | 138 | 97.9 |  | 97.9 |  | 98.6 |  | 98.6 |  | 98.4 |  | 98.4 |  | 94.6 |  | 94.6 |  | 97.9 |  | 97.9 |  | 97.4 |  | 97.4 |  | 96.2 |  | 96.2 |  | 94.4 | <90 | 94.4 | 92.8 | <90 | 92.8 | 20309 BISCOE W 230 20332 ASHEB 230 1 | New project (uprate)
Camden-Camden Junction 115 kV | 20725 CAMDEN 115 20731 I-DUP CA 115 1 | 83.3 | 80.2 | 83.3 | 2017.68 | Beyond /Follow | 98.4 | 15.1 | SC | 6.04 | 2011.64 | 108 |  |  |  |  | 98 | 94.7 | 98 | 5.88 | 98.4 | 95.2 | 98.4 | 6.04 | [22 empty] | 20716 CAMCTY02 115 20725 CAMDEN 115 1 | New project (uprate)
Durham-Cary Reg Pk 230 | 20091 BRIERCK 230 10159 RTP 23KV 230 1 | 88.7 | 70.5 | 88.7 |  | OpProc3 | 98.3 | 9.6 | Duke |  | 2011.68 | 539 | 98.3 |  | 98.3 |  | 94.8 |  | 94.8 |  | 94.8 |  | 94.8 |  | 95.7 |  | 95.7 |  | 95.8 |  | 95.8 |  | 96.1 |  | 96.1 |  | 96.5 |  | 96.5 |  | 95.6 | <90 | 95.6 | 94.9 | <90 | 94.9 | METHOD-PRISONF230_&_METHOD-BLUERDG230 | New project
Tilley-Biscoe 115 kV | 20683 BURNETTE 115 20301 TROY 115 1 | 89.1 | 75.8 | 89.1 |  | OpProc1 | 98 | 8.9 | Duke |  | 2011.8 | 269 | 98 |  | 98 |  | 96.8 |  | 96.8 |  | 96.1 |  | 96.1 |  | 92.9 |  | 92.9 |  | 96.7 |  | 96.7 |  | 96.3 |  | 96.3 |  | 95 |  | 95 |  | 92.5 | <90 | 92.5 | 90.4 | <90 | 90.4 | 20347 ABRDN RD 230 20348 RKH 230 1 | Operating Procedure
Rockingham-West End 230 kV Line | 20638 WDSB T 230 20360 ELLERBE 230 1 | 91.8 | 78.2 | 91.8 |  | OpProc5 | 97.7 | 5.9 | SC |  | 2011.92 | 507 | 95.4 |  | 95.4 |  | 97.5 |  | 97.5 |  | 97.7 |  | 97.7 |  | 93.8 |  | 93.8 |  | 96.6 |  | 96.6 |  | 96.1 |  | 96.1 |  | 95.1 |  | 95.1 |  | 93.9 | <90 | 93.9 | 92.7 | <90 | 92.7 | 20348 RKH 230 20361 WEST END 230 1 | New project (uprate)
Fall-Franklinton 115kV | 20185 FALLS 115 20111 E18-WK F 115 1 | 92 | 94.7 | 94.7 |  | OpProc4 | 97.6 | 2.9 | Duke |  | 2011.96 | 170 | 94.7 | 97.6 | 97.6 |  | 94.2 | 97.1 | 97.1 |  | 94 | 97 | 97 |  | 92.2 | 95 | 95 |  | 94 | 97 | 97 |  | 93.9 | 96.9 | 96.9 |  | 93.6 | 96.5 | 96.5 |  | 92.9 | 95.7 | 95.7 | 91.4 | 94.3 | 94.3 | 20089 HENDERSN 115 20105 FRANKLIN 115 1 | Local /Follow
Sutton-Castle Hayne 230kV | 20577 MURRAYVL 230 20552 E WILM 230 1 | 90 | 85.7 | 90 |  | OpProc2 | 97.5 | 7.5 | AEP/AEP |  | 2012 | 590 | 90.4 |  | 90.4 |  | 91.1 |  | 91.1 |  | 91.1 |  | 91.1 | [5 empty] | 90.7 |  | 90.7 |  | 90.5 |  | 90.5 |  | 90.2 |  | 90.2 |  | 97.5 | 93.3 | 97.5 |  |  |  | BR1-BARCK230_&_BR2-BARCRK230 | Local /Follow
Marion Whiteville 115 kV | 20632 MARION 115 20630 MULLINS 115 1 | 69.5 | 81.9 | 81.9 | 2018.24 | Beyond /Follow | 97.4 | 15.5 | SC | 6.2 | 2012.04 | 179 |  |  | 0 |  |  | 94.8 | 94.8 | 5.16 |  | 97.4 | 97.4 | 6.2 | [5 empty] | 90.6 | 90.6 | 3.48 |  |  | 0 | [5 empty] | <90 | 90.1 | 90.1 | <90 | <90 | 0 | 20587 E1-CHADP 230 20631 MARION 230 1 | New project (rebuild/ recond)
West End-Cape Fear 230 kV | 20314 E3-CTRCH 230 20361 WEST END 230 1 | 86.9 | 70.4 | 86.9 | 2016.24 | Beyond /Follow | 96 | 9.1 | SCEG | 3.64 | 2012.6 | 507 | 92.8 |  | 92.8 | 2.36 | 96 |  | 96 | 3.64 | 95.9 |  | 95.9 | 3.6 |  |  |  |  | 94.6 |  | 94.6 | 3.08 | 93.8 |  | 93.8 | 2.76 | 91.9 |  | 91.9 | 2 | [6 empty] | 20377 RICHMOND 500 20391 CUMBERLD 500 1 | New proj (rebuild/ recond)
Method-E. Durham 230 kV | 20076 LEESVILL 230 845 6E.DURHM 230 1 | 81.6 | 74.3 | 81.6 | 2018.36 | Beyond /Follow | 95.8 | 14.2 | Duke | 5.68 | 2012.68 | 745 | 95.8 |  | 95.8 | 5.68 |  |  | 0 | [27 empty] | 845 6E.DURHM 230 20117 DURHAM 230 1 | New project (replace equip/recond)
Chestnut Hills-Milburnie 115 | 20155 CHSTNT H 115 20163 MILBURNE 115 1 | 94.3 | 93.9 | 94.3 | 2013.28 | Local /Follow | 95.7 | 1.4 | SCEG/SOCO | 0.56 | 2012.72 | 158 | 95.6 | 95.2 | 95.6 | 0.52 | 95.7 | 95.2 | 95.7 | 0.56 | 95.6 | 95.1 | 95.6 | 0.52 | 95.2 | 94.8 | 95.2 | 0.36 | 95.7 | 95.2 | 95.7 | 0.56 | 95.6 | 95.2 | 95.6 | 0.52 | 95.5 | 95.1 | 95.5 | 0.48 | 95.4 | 95 | 95.4 | 95.1 | 94.7 | 95.1 | 20145 NEUSE 115 20185 FALLS 115 1 | Local /Follow
Method-E. Durham 230 kV | 20073 BLUE RDG 230 20124 METHOD 230 1 | 78.8 | 70.4 | 78.8 | 2019.48 | Beyond /Follow | 95.1 | 16.3 | Duke | 6.52 | 2012.96 | 637 | 95.1 |  | 95.1 | 6.52 |  |  | 0 |  |  | 91.4 | 91.4 | 5.04 | [22 empty] | 845 6E.DURHM 230 20117 DURHAM 230 1 | New project (replace equipment)
Milburnie-Person 230 kV | 20066 FALLS23 230 20097 CG-ROX 230 1 | 86.8 | 85.9 | 86.8 | 2016.28 | Beyond /Follow | 94.9 | 8.1 | AEP/AEP | 3.24 | 2013.04 | 423 | 94.8 | 93.8 | 94.8 | 3.2 | 93.2 | 92 | 93.2 | 2.56 | 92.6 |  | 92.6 | 2.32 | 93 | 91.9 | 93 | 2.48 | 93.9 | 92.8 | 93.9 | 2.84 | 94.1 | 93 | 94.1 | 2.92 | 94.6 | 93.4 | 94.6 | 3.12 | 94.9 | 93.8 | 94.9 | 93.4 | 92.3 | 93.4 | 20015 MAYO 1F 500 20054 DURHAM 500 1 | New project (uprate)
Durham-Cary Reg Pk 230 | 20126 MORRISVI 230 20159 RTP 23KV 1 | 84.6 | 66.5 | 84.6 |  | OpProc3 | 94.1 | 9.5 | Duke |  | 2013.36 | 539 | 94.1 |  | 94.1 |  | 90.6 |  | 90.6 |  | 90.6 |  | 90.6 |  | 91.5 |  | 91.5 |  | 91.6 |  | 91.6 |  | 91.9 |  | 91.9 |  | 92.3 |  | 92.3 |  | 91.4 | <90 | 91.4 | 90.7 | <90 | 90.7 | METHOD-PRISONF230_&_METHOD-BLUERDG230 | New project
West End-Cape Fear 230 kV | 20314 E3-CTRCH 230 20373 S GARD T 230 1 | 84.5 | 68.1 | 84.5 | 2017.2 | Beyond /Follow | 93.5 | 9 | SCEG | 3.6 | 2013.6 | 507 | 90.4 |  | 90.4 |  | 93.5 |  | 93.5 |  | 93.4 |  | 93.4 | [5 empty] | 92.1 |  | 92.1 |  | 91.3 |  | 91.3 | [11 empty] | 20377 RICHMOND 500 20391 CUMBERLD 500 1 | New proj (rebuild/ recond)
Weatherspoon-Fay DuPont 115 | 20047 WSP BUS 115 20406 ST PAULS 115 1 | 82.4 | 67.2 | 82.4 | 2018.04 | Beyond /Follow | 93.1 | 10.7 | SC | 4.28 | 2013.76 | 119 |  |  |  |  | 91.6 |  | 91.6 | 3.68 | 93.1 |  | 93.1 | 4.28 | [22 empty] | FAY-HAMLET230_&_RAEFORD-ROCKFISH230 | New project (replace equip/recond)
Rockingham-West End 230 kV Line | 20360 ELLERBE 230 20361 WEST END 230 1 | 86.9 | 73.4 | 86.9 | 2016.24 | Beyond /Follow | 92.8 | 5.9 | SC | 2.36 | 2013.88 | 507 | 90.5 |  | 90.5 | 1.44 | 92.6 |  | 92.6 | 2.28 | 92.8 |  | 92.8 | 2.36 |  |  |  |  | 91.7 |  | 91.7 | 1.92 | 91.2 |  | 91.2 | 1.72 | 90.2 |  | 90.2 | 1.32 | [6 empty] | 20348 RKH 230 20361 WEST END 230 1 | New project (uprate)
Tilley-Biscoe 115 kV | 20428 BISCOE W 115 20301 TROY 115 1 | 83.8 | 70.7 | 83.8 |  | OpProc1 | 92.6 | 8.8 | Duke |  | 2013.96 | 269 | 92.6 |  | 92.6 |  | 91.4 |  | 91.4 |  | 90.7 |  | 90.7 | [5 empty] | 91.2 |  | 91.2 |  | 90.9 |  | 90.9 | [11 empty] | 20347 ABRDN RD 230 20348 RKH 230 1 | Operating Procedure
Method-Milburnie 115 kV South | 20168 YONKERS 115 20163 MILBURNE 115 1 | 91.3 | 91 | 91.3 | 2014.48 | Local /Follow | 92.6 | 1.3 | SCEG/SOCO | 0.52 | 2013.96 | 190 | 92.5 | 92.2 | 92.5 | 0.48 | 92.6 | 92.2 | 92.6 | 0.52 | 92.5 | 92.1 | 92.5 | 0.48 | 92.2 | 91.8 | 92.2 | 0.36 | 92.6 | 92.2 | 92.6 | 0.52 | 92.5 | 92.1 | 92.5 | 0.48 | 92.4 | 92.1 | 92.4 | 0.44 | 92.3 | 92 | 92.3 | 92.1 | 91.8 | 92.1 | 20137 METHOD 115 20150 I-NCSU S 115 1 | Local /Follow
Florence -Latta 230 kV | 20662 FLORENCE 230 20663 LATTA 230 1 | 67.1 | 77.8 | 77.8 | 2019.88 | Beyond /Follow | 92 | 14.2 | SC | 5.68 | 2014.2 | 507 | [5 empty] | 90.8 | 90.8 | 5.2 |  | 92 | 92 | 5.68 | [6 empty] | 0 | [15 empty] | MARION-MARION(SCPSA)230_1&2 | Operating Procedure
Clinton - Vander 115 kV | 20401 VANDER 115 20265 E15-STED 115 1 | 65.4 | 77.4 | 77.4 | 2020.04 | Beyond /Follow | 91.5 | 14.1 | SC | 5.64 | 2014.4 | 163 |  |  | 0 |  |  | 91.2 | 91.2 | 5.52 |  | 91.5 | 91.5 | 5.64 | [5 empty] | 90.4 | 90.4 | 5.2 |  | 90 | 90 | 5.04 |  |  | 0 | [7 empty] | 20196 ERWIN 230 20197 DUNN 230 1 | Operating Procedure
Henderson-Franklin 115 | 20089 HENDERSN 115 20105 FRANKLIN 115 1 | 86 | 87.3 | 87.3 | 2016.08 | Beyond /Follow | 91 | 3.7 | Duke | 1.48 | 2014.6 | 201 |  | 91 | 91 | 1.48 |  | 90.3 | 90.3 | 1.2 |  | 90.1 | 90.1 | 1.12 | [5 empty] | 90.5 | 90.5 | 1.28 |  | 90.5 | 90.5 | 1.28 |  | 90.5 | 90.5 | 1.28 | <90 | 90.3 | 90.3 | <90 | <90 | 0 | 20111 E18-WK F 115 20185 FALLS 115 1 | Local /Follow
Cumberland 500/230 Bank | 20391 CUMBERLD 500 B$0005 1.00 1 | 78 | 84.8 | 84.8 | 2020.68 | Beyond /Follow | 90.6 | 5.8 | Duke | 2.32 | 2018.36 | 1000 |  | 90.6 | 90.6 | 2.32 |  |  | 0 | [10 empty] | 90.4 | 90.4 | 2.24 |  | 90.3 | 90.3 | 2.2 | [10 empty] | 20183 WAKE 500 20391 CUMBERLD 500 1 | Beyond horizon
Method-Milburnie 115 kV South | 20137 METHOD 115 20150 I-NCSU S 115 1 | 89.3 | 88.7 | 89.3 | 2015.28 | Local /Follow | 90.6 | 1.3 | SOCO | 0.52 | 2014.76 | 190 | 90.3 |  | 90.3 | 0.4 | 90.4 |  | 90.4 | 0.44 | 90.3 |  | 90.3 | 0.4 |  |  |  |  | 90.6 |  | 90.6 | 0.52 | 90.3 |  | 90.3 | 0.4 | 90.6 |  | 90.6 | 0.52 | 90 | <90 | 90 | <90 | <90 | 0 | 20163 MILBURNE 115 20168 YONKERS 115 1 | Local /Follow
Method 230/115 1 & 2 | 20137 METHOD 115 20124 METHOD 230 1/2 | 78.7 | 85 | 85 | 2020.6 | Beyond /Follow | 90 | 5 | Duke | 2 | 2018.6 | 300 |  | 90 | 90 | 2 |  |  | 0 | [27 empty] | 20124 METHOD 230 20137 METHOD 115 2/1 | Beyond horizon
Note on B3: PTI: ** From bus ** ** To bus ** Circuit Type
Note on M3: PTI: Branch Rating
Note on N3: PTI: Loading in %
Note on O3: PTI: Loading in %
Note on R3: PTI: Loading in %
Note on S3: PTI: Loading in %
Note on V3: PTI: Loading in %
Note on W3: PTI: Loading in %
Note on Z3: PTI: Loading in %
Note on AA3: PTI: Loading in %
Note on AD3: PTI: Loading in %
Note on AE3: PTI: Loading in %
Note on AH3: PTI: Loading in %
Note on AI3: PTI: Loading in %
Note on AL3: PTI: Loading in %
Note on AM3: PTI: Loading in %
Note on AV3: PTI: Contingency Description