Project Name:	Parkwood 500/230 kV transformers

Project Description

Increase transformer capacity to alleviate congestion.

| Projected In-Service Date for Base Reliability Plan | 2015 |
| --- | --- |
| Earliest Projected In-Service Date For Resource Supply Option | 2011 600 MW Import to CPLE from Duke |
| Project Lead Time | 5 years |
| Estimated Cost | $15 – 20 M |

Narrative Description of the Need for this Project

The Parkwood banks will achieve 100% of their present rating (840 MVA) in the 2011-2017 timeframe. Loss of the parallel bank when there is a loss of a large generator on the Duke system causes the highest loading. West to east transfers across the Duke control area increase bank loading and limit export capability to CPLE. Bank 5 has issues with stray flux heating. Bank 6 is a newer bank with a higher rating. It is expected that both banks would be changed out simultaneously with higher capacity banks.

Transmission Solutions Considered

First, perform testing/analysis of bank 5 to eliminate the stray flux heating concern and allow re-rating of the bank closer to the original design. Based on outcome of testing/analysis, replace of the banks with higher capacity banks, if necessary.

Why this Project was Selected as the Preferred Solution

The banks have an ~10% OTDF. For each incremental increase in the rating by 10 MVA, there will be an increase in transfer capability of 100 MW. Evaluation of the stray flux issue may lead to a significant delay in when their replacement may be necessary.